## Slide 1: EECS 290O
April 1 2019 Slides
Generator control
Load models
Next steps

## Slide 2: Schedule
Week | Paper group | Book reading | Notes
Apr 1 | Ramasubramanian | MBB 11 | 
Apr 8 | Lin | Y&I 2-3 | 
Apr 15 | Curi | Y&I 4-5 | 
Apr 22 | Ramasubramanian | Y&I 8 | 
Apr 29 | Lin and Markovic | TBD | Duncan travelling!

## Slide 3: Agenda for today
Ramasubramanian group presentation
MBB wrapup: High level discussion of Ch 11:
  Controlling voltage excitation
  Power / frequency regulation
  Dynamic loads
Begin discussing voltage source converters
  Discuss pace for upcoming weeks

## Slide 4: Sixth order model for generator (11.101)
All quantities are per-unit
Generator control: influences Ef and Pm
Loads and transmission system: influences Pe

## Slide 5: Next: Ef (Excitation systems and control)
Objectives:
  Review basic design architectures
  Discuss feedback control loops
  Understand structure of generic ODE formulations

## Slide 6: Excitation systems come in many flavors

## Slide 7: DC excitation control block (Fig 2.3a; these are older devices)
SE = constant -> Simple first order system
But SE can be used to model saturation effects in exciter iron

## Slide 8: Adding voltage regulation adds more first order blocks
(Don’t sweat the details)
Main takeaway: regulator control structure is linear, simple to model and analyze (with patience)

## Slide 9: Alternative exciter / AVRs and power system stabilization
New systems (not equal to an average extant system) use “static” exciters
  That means electronic switches are used to produce DC waveform
  Basic modeling process is the same –
    A sequence of first order control blocks
    With possible built-in nonlinear mappings for saturation effects
Power system stabilization:
  Vary voltage reference into AVR to produce a torque component that is in phase (and opposing) rotor speed deviation

## Slide 10: Now: Pm (generator mechanical power control)
Steam turbines:
  Regulate heat to a boiler
  Produce steam
  Regulate steam delivered to turbines
  Turbines produce torque in proportion to mass flow rate of steam
Two regulation processes above: which to adjust to vary turbine torque?
  Hint: think like a bagpiper

## Slide 11: Basic turbine dynamics building block
Once again, basic first order dynamics govern changing steam mass flow rate
…and mass flow is proportional to turbine torque.

## Slide 12: Things get hairy fast…
But the basic idea is simple: adjust valve position in response to speed deviation with proportional gain as driving control.
  Objective is to get linear relationship between speed deviation and electrical power

## Slide 13: Load models (Pe)
“Static” load models
  Constant impedance
  Constant current
  Constant power
  There are frequency-dependent variations of this
  Equations from “Standard Load Models for Power Flow and Dynamic Performance Simulation”, IEEE Trans Pow Sys, 1995
Constant energy loads
  Typically thermostatically controlled
  Might be voltage dependent instantaneously, but energy over time doesn’t change
  Don’t matter much for short time scale dynamic studies

## Slide 14: Load models (Pe)
Dynamic load models
  Synchronous motors: familiar generators in reverse
  Induction motors
    emf supplied by slip 

## Slide 15: Load composition
Constant impedance:
  incandescent lighting, and other anachronistic loads
Constant current:
  Arc lamps, and other anachronistic loads
Dynamic induction motors:
  This doesn’t include motors with variable frequency drives
  …perhaps not completely obsolete, but certainly losing market share
What’s left in the future?
  Constant power loads, thanks to power electronic converters.
Moral of the story:
  Proper load modeling getting less complex
  …But plenty of people still model loads as solely constant impedance

## Slide 16: Looking ahead: What’s next?

## Slide 17: Option 1 (current plan): VSCs
Week | Book reading | Notes
Apr 8 | Y&I 2-3 | Half bridge converter models (2) and control (3) Current control, feedforward control, sinusoidal command following
Apr 15 | Y&I 5-6 | 5: Two-level Three phase converter. Model and control in dq (quick treatment) 6: Neutral point clamped three level three phase converter Switched model, averaged model, dc-side eqns
Apr 22 | Y&I 8 | dq-control, grid imposed frequency PLL Current control mode AC side equivalent circuit
Apr 29 | TBD | Duncan travelling!

## Slide 18: Option 2: Explore alternative topics
Theory
  Energy function methods for transient stability
Engineering
  Transmission line dynamic models
Scripting
  Milano’s text,
  Methods for harmonizing our models – cf earlier discussion from Rama group
Review / present / discuss planning docs for high penetration renewable areas
  Eirgrid
  ERCOT
Multimachine models

## Slide 19: Options going forward
Continue reviewing text book and Duncan summarizes, now for Y&I rather than MBB
  Power electronics folks might be bored?
We can pick and choose from some of the alternative topics listed on the last page
Power electronics folks could deliver Y&I content – to keep from getting bored, and to ensure stronger expertise at the board!